BFPRODUCTS, INC.

# BACKFLOW PREVENTION DEVICE ENCLOSURES FOR ABOVE GROUND INSTALLATIONS

# “WE’VE GOT YOU COVERED” Tech #704-599-9407

INSTALLATION INSTRUCTIONS – Small Series

#191-APD, #271-APD, #371-APD, #232-APD, #322-APD

CONCRETE PAD/FOOTER:

- CREATE AND CENTER A MINIMUM 4" THICK CONCRETE PAD/FOOTER  AROUND THE INSTALLED DEVICE PLACING EXPANSION MATERIAL AROUND THE DEVICE RISER PIPES(see chart below for recommended pad dimensions).

- CENTER ENCLOSURE OVER THE DEVICE ON THE CONCRETE PAD.

- WITH MASONRY BIT DRILL 1/4" HOLES THROUGH ENCLOSURE BASE FLANGE (ONE EACH SIDE) INTO PAD/FOOTER

- INSERT 1/4" X 21/2" THREADED ANCHOR SPIKE IN DRILLED HOLE. TAP WITH HAMMER UNTIL ANCHOR SPIKE THREADS EXTEND 1/2" ABOVE ENCLOSURE FLANGE BASE.

- SECURE ENCLOSURE TO CONCRETE PAD WITH ANCHOR SPIKE NUTS AND WASHERS.

Model #	191-APD   271-APD   371-APD   232-APD   322-APD

Pad Size   	26 x 17     38 x 20      48 x 25      36 x 20      46 x 23

GROUND / TURF / DIRT:  ( T-TURF - Elevated discharge drain)

1.	PLACE ENCLOSURE OVER THE DEVICE CENTERED ON THE

GROUND/TURF /DIRT.

2.	COVER ENCLOSURE BASE FLANGE WITH GROUND/TURF/DIRT.

OPTIONAL HEAT SOURCE NOTE:

#H-30 & #H-90 - 120V, PRE-ASSEMBLED ELECTRIC HEATING CABLE, INSTALLATION INSTRUCTIONS FOR THE ELECTRICAL HEAT SOURCE ARE INCLUDED WITH HEATER.

WARNING!

A GROUND FAULT CIRCUIT INTERRUPTING DEVICE SHALL BE 			INSTALLED IN THE ELECTRICAL SUPPLY CIRCUIT TO THIS 				HEATER.  FAILURE TO DO SO MAY RESULT IN INJURY OR 					DEATH.  THE INTERIOR OF THIS ENCLOSURE IS A DAMP LOCATION.